## Slide 1
How Much Does Seawater Desalination Cost?
Water Globe Consulting
Nikolay Voutchkov, PE, BCEE

## Slide 2: Presentation Outline
Overview of Current Desalination Cost Trends
Low-Cost Bracket Desalination Projects – Key Features
High-Cost Bracket Desalination Projects – What Factors Drive the High Costs?
Key Cost Components
Main Factors Impacting Costs

## Slide 3: Cost of Water of Recent Desalination Projects
Chart: Cost of Water , US$/kgal
| 108 MGD Sorek, Israel | 132 MGD Mactaa, Algeria | 87 MGD Hadera, Israel | 98 MGD Askelon, Israel | 0.6 MGD Sand City, CA | 50 MGD Hamma, Algeria | 25 MGD Tampa Bay, FL | 45 MGD Fujairah, UAE | 50 MGD Carlsbad, CA | 53 MGD Barcelona, Spain | 38 MGD Perth I, Australia | 66 MGD Sydney, Australia | 40 MGD Perth II, Australia | 108 MGD Melbourne, Australia | 35 MGD Gold Coast, Australia | 40 MGD Adelaide, Australia
Cost of Water US$/kgal | 2.01 | 2.12 | 2.27 | 2.3 | 2.91 | 3.15 | 3.48 | 3.55 | 4 | 4.38 | 4.4 | 7.32 | 8.33 | 9.54 | 10.98 | 11.36

## Slide 4: Costs of Recent US SWRO Projects
Project | Status | Capital Cost (US$) | Annual O&M Cost (US$/kgal) | Cost of Water (US$/kgal)
0.6 MGD Sand City, CA | In Operation since 2010 | US$11.9 MM | US$1.15/kgal | US$2.91/kgal
25 MGD Tampa Bay, FL | In Operation since 2008 | US$138 MM | US$1.54/kgal | US$3.48/kgal
50 MGD Carlsbad, CA | In Financing | US$350 MM | US$1.75/kgal | US$4.00/kgal
2.5 MGD Santa Cruz, CA | In Planning | US$59-64 MM | US$3.94/kgal | US$7.6-8.0/kgal
2.5 MGD Brownsville Demo Project, TX | In Planning | US$22.5 MM | US$2.80/kgal | US$4.38/kgal
25 MGD-80 MGD Coquina Coast, FL | In Planning | US$180 MM -US$560 MM | US$1.99/kgal | US$4.47/kgal (US$5.35-US$6.10 w/ conveyance)

## Slide 5: Typical Cost and Energy Ranges (Medium & Large SWRO Plants)
Classification | Cost of Water Production (US$/kgal) | SWRO System Energy Use (US$/kgal)
Low-End Bracket | 2.0 - 3.0 | 9.5 – 10.5
Medium Range | 3.5 – 5.0 | 11.0 - 12.0
High-End Bracket | 6.5 - 11.5 | 12.5 – 14.0
Average | 4.0 | 11.5

## Slide 6: Common Features of Low-Cost Desalination Projects
Low Cost HDPE Open Intakes or Beach Wells;
Near-Shore/On-Shore Discharges w/o Diffuser Systems or Co-discharge w/ Power Plant of WWTP Outfalls;
Point of Product Water Delivery within 5 Miles of Desalination Plant Site;
RO System Design w/ Feed of Multiple Trains by Common High Pressure Pumps and Energy Recovery Systems;
Turnkey (BOOT, BOO) Method of Project Delivery.

## Slide 7: Key Reasons for Cost Disparity Between High-End & Low-end Cost Projects (US$2.0 – 3.0 vs. US$6.5-11.5/kgal)
Desalination Site Location (NIMBI vs. Science Driven)
  Costly Plants Have Overly Long Product Water Delivery Pipelines
    120 MGD Melbourne Plant – Cost of Plant/Delivery + Power Supply Systems =
    US$1.7 BB/1.1 BB (50 miles)
    66 MGD Sydney SWRO Plant – Cost of Plant/Delivery System
    = US$560 MM/US$490 MM (10 miles of underground tunnel under Botany Bay).
Environmental Considerations
  Complex Intakes & Diffuser Systems
Phasing Strategy
  Intake and Discharge System Capacity;
  Pretreatment & RO System Design;
Labor Market Pressures
Method of Project Delivery & Risk Allocation
Notes: 7

## Slide 8: Seawater Desalination Plant – Construction Costs
Intake – 5 to 20 %
of Construction Costs
Discharge – 5 to 15 %
of Construction Costs
RO System –
40 % to 60 % of
Construction Costs
Pretreatment –
15% to 20 %
of Construction costs
Notes: 8

## Slide 9: Intake Construction Costs Key Factors
Very Dependent on Source Water Quality
Usually US$0.5 – 1.5 MM/MGD (up to 3.0 MM/MGD for Complex Tunnel Intakes)
Beach Well Intakes Are Usually Less Costly
Horizontal and Slant Wells Comparable to Open Intakes
Infiltration Galleries Often are More Expensive than Open Intakes

## Slide 10: Pretreatment Construction Costs
Very Dependent on Source Water Quality & Type of Treatment Technologies
Usually US$0.5 – US$1.5 MM/MGD
High Quality Well Water Sources Require Only Cartridge Filtration (Low Cost Pretreatment)
Single-stage Granular Media Filtration Usually is Less Costly than Membrane Pretreatment

## Slide 11: SWRO System Construction Costs
Dependent on Source Water Quality & Target Product Water Quality
Usually Between US$1.5-4.0 MM/MGD
Single-stage/Single Pass SWRO System is Least Costly
Additional Costs for Two-Pass/Two-Stage RO System May Vary Between 15 and 30 % of the These of Single Pass/Single Stage SWRO System

## Slide 12: Concentrate Disposal Construction Costs
Disposal Method | Construction Cost (US$ Million/MGD)
New Outfall w/Diffusers | 2.0 – 5.5
Power Plant Outfall | 0.2 – 0.6
Sanitary Sewer | 0.1 – 0.4
WWTP Outfall | 0.3 – 2.0
Deep Well Injection | 2.5 – 6.0
Evaporation Ponds | 3.0 – 9.5
Zero-Liquid Discharge | 5.5 – 15.0

## Slide 13: Typical O&M Cost Breakdown
Chart: 
| Energy | Chemicals | RO/CF Replacement | Sludge Disposal | Labor | Maintenance | Env. Monitoring | Other
O&M Costs (%) | 55.5 | 6 | 10.6 | 4.4 | 5.7 | 6.5 | 1.5 | 9.8
Usual O&M Cost Range
US$1.5 – 4.0/kgal

## Slide 14: Cost of Water Breakdown
Chart: 
| RO System Constr. Cost | Power Cost | Intake & Discharge Constr. Cost | Pretreatment Constr. Cost | Project Eng. & Permitting | RO/CF Replacement | Other Costs
Column1 | 0.305 | 0.26 | 0.105 | 0.12 | 0.065 | 0.058 | 0.087

## Slide 15: Key Factors Affecting Costs
Plant Size – Bigger is Better
Source Water Quality - TDS, Temperature, Solids, Silt and Organics Content.
Product Water Quality – TDS, Boron, Bromides, Disinfection Compatibility.
Concentrate Disposal Method;
Power Supply & Unit Power Costs;
Project Delivery Method & Financing;
Other Factors:
  Intake and Discharge System Type;
  Pretreatment & RO System Design;
  Plant Capacity Availability Target.
Notes: 15

## Slide 16: Desalination Plant Construction Cost as Function of Capacity
Chart: Unit Construction Cost (US$ MM/MGD)
| 0.5 MGD | 1 MGD | 2 MGD | 5 MGD | 10 MGD | 20 MGD | 50 MGD | 100 MGD
Unit Construction Cost (US$ MM/MGD) | 13.9 | 11.8 | 10.2 | 8.8 | 8.2 | 7.2 | 6.7 | 6.4

## Slide 17: Product Water Quality & Costs
Target WQ | Constr. Costs | O&M Costs | Cost of Water
TDS/Cl = 500/250 mg/L; Boron = 1 mg/L. | 1.0 | 1.0 | 1.0
TDS/Cl = 250/100 mg/L; Boron = 0.75 mg/L. | 1.15-1.25 | 1.05-1.10 | 1.10-1.18
TDS/Cl = 100/50 mg/L; Boron = 0.5 mg/L. | 1.27-1.38 | 1.18-1.25 | 1.23-1.32
TDS/Cl = 30/10 mg/L; Boron = 0.3 mg/L. | 1.40-1.55 | 1.32-1.45 | 1.36-1.50
Notes: 17

## Slide 18: Where Future Cost Savings Would Come From?
Notes: 18

## Slide 19: “The Best” of Seawater Desalination Present Status & Future Forecasts
Parameter | Today | Within 5 Years | Within 20 Years
Cost of Water (2010 US$/kgal) | US$2.0-3.0 | US$1.5-2.5 | US$1.0-1.5
Construction Cost (Million US$/MGD) | 4.5-8.0 | 4.0-6.5 | 2.0-3.5
Power Use of SWRO System (kWh/kgal) | 9.5-10.5 | 8.0-10.0 | 5.0-6.5
Membrane Productivity (gallons/day/membrane) | 6,500-12,500 | 9,000-15,000 | 25,000-40,000
Membrane Useful Life (years) | 5-7 | 7-10 | 10-15
Plant Recovery Ratio (%) | 45-50 | 50-55 | 55-65
Notes: 19

## Slide 20: Concluding Remarks
Seawater Desalination is Economical Today and Will Become Even More Cost-Competitive in the Future;
Typical Cost of Water is US$3.5 to US$5.0/kgal;
The Future of Seawater Desalination Is Bright – 20% Cost of Water Reduction in the Next 5 Years;
Long-term Investment In Research and Development Has the Potential to Reduce the Cost of Desalinated Water by 80 % In the Next 20 Years.
Notes: 20

## Slide 21: Seawater Desalination Costs
Questions?