## Slide 1: What is the appropriate balance between conventional treatment and environmental buffers?
Betty Jordan, P.E.
Texas Water Development Board
Texas Innovative Water 2010 Seminar
October 11-12, 2010

## Slide 2
To treat or not to treat –
That is not the question.

## Slide 3: So what is the question?

## Slide 4: How much treatment is required for safe and effective water reuse ?
Historically
  What is the end use of the water?
  What quality requirements are needed for the end use?
Today
  What is the end use of the water?
  What quality requirements are needed for the end use?
    Some things we know for certain.
    Some things we don’t know.
  What does the public require for the use?

## Slide 5: What is being removed?
Conventional Pollutants
Nutrients
Minerals/Salts
Pathogens
Metals
Microconstituents

## Slide 6: What processes remove what?
Activated Carbon
Biologically Activated Carbon
Clarification/Flocculation
Softening
Ozone
Ozone with Advanced Oxidative Processes
Ultraviolet Radiation
Chlorine/Hypochlorite
Microfiltration
Reverse Osmosis
Wetlands
Aquifer Sand Filtration
Activated Sludge
Membranee Bioreactors

## Slide 7: Removal Efficiencies – Conventional Processes
PhAC Class | AC | BAC | C/F | Soft.
Antibiotics | 40-90% | >90% | <20-40% | <20-40%
Anti-depressants | 70->90% | 70->90% | <20-40% | <20-40%
Anti-infalamants | >90% | 70->90% | <20% | <20-40%
Lipid Regs. | >90% | >90% | <20% | <20-40%
X-ray contrast media | <70-90% | 70-90% | <20-40% | <20-40%
Psychiatric Control | 70->90% | 70-90% | <20-40% | <20-40%
Yoon, Westerhoff, Snyder, Song, Levine, AWWA WQQTC, 2004

## Slide 8: Removal Efficiencies – Conventional Processes
EDC Class | AC | BAC | C/F | Soft.
Pesticides | >90% | >90% | <20 | 70-90%
Ind. Chem | >90% | >90% | <20-40% | <20-40%
Steroids | >90% | >90% | <20% | <20-40%
Metals | 70-90% | 70-90% | 40-90% | 40-90%
Inorganics | <20-40% | 40-70% | <20% | 70-90%
Organo-metalics | 70->90% | 70-90% | <20-40% | <20-40%
Yoon, Westerhoff, Snyder, Song, Levine, AWWA WQQTC, 2004

## Slide 9: Removal Efficiencies – Oxidation & Membranes
EDC Class | O3/AOPs | UV | CL2/CLO2 | MF | RO
Pesticides | 20->90% | >90% | 70->90% | 70-90% | >90%
Ind. Chem | 40-90% | >90% | <20% | >90% | >90%
Steroids | >90% | >90% | >90% | 70-90% | >90%
Metals | <20% | <20% | <20% | 70-90% | >90%
Inorganics | <20% | <20% | <20% | 70-90% | >90%
Organo-metalics | 20-90% | 40-90% | 40-90% | 70-90% | >90%
Yoon, Westerhoff, Snyder, Song, Levine, AWWA WQQTC, 2002

## Slide 10: Activated Sludge/MBRs
Hydraulic Detention Time
Sludge Age

## Slide 11: Natural Systems
Wetlands
  Nutrients
  Suspended solids
  Organics
  Microconsituents
Soil Filtration
  Nutrients
  Suspended Solids
  Organics
  Microconstituents

## Slide 12: Conventional Direct Reuse
Bar Screens
Grit
Removal
Filters
Activated
Sludge
Primary
Clarification
Final Clarification
Disinfection
Conventional Reuse applications:
Landscape irrigation
Industrial supply

## Slide 13: Indirect Potable Reuse
Advanced
Secondary or
Tertiary
Effluent
AOP
MF/UF
Carbon
Filtration
RO
Wetlands
Reservoir
Reservoir
Aquifer
Storage
Aquifer
Storage
Reservoir

## Slide 14
We are the guardians of public health.
We are the guardians of the environment.
We are the stewards of public finance.

## Slide 15: Contact information: Betty L. Jordan, P.E. Alan Plummer Associates, Inc. Phone: 214.631.6100 Email: bjordan@apaienv.com