Water Loss Audit Help Form

(All numbers used in this worksheet are for example purposes only)

The following instructions can be used in completing the Water Audit Worksheet. The instructions are labeled by line number shown on the worksheet. The Water Audit Worksheet requests that the water utility enter general information and water supply, consumption, and loss quantities. It also requests assessment scores representing the degree of validation of individual components. For those components that include an assessment line, enter a number between 0.5 and 5. (See Appendix 1.3 for more information). If a component does not apply, then select N/A (for example, if the water utility does not purchase any treated water, select N/A for Total Treated Purchased Water). You may visit the TWDB Web site for the online version of the water audit: http://www.twdb.texas.gov/conservation/municipal/waterloss/index.asp.

- Water Utility Information

  - Water Utility Name: Lists the formal name of the water utility for which the water audit exists. 1a. Regional Water Planning Area: Select the RWP Area (A through P) into which your utility falls (see

map at http://www.twdb.texas.gov/mapping/doc/maps/RWPAs_8x11.pdf).

1b. Address: Complete the address with street name, city state and zip code.

  - Contact: Displays the name of the person completing the water audit (2a.), including email address (2b.) and telephone number (2c.).

  - Reporting Period: Enter calendar year dates for the reporting period. (3a.) Start Date and (3b.) End Date.

  - Source Water Utilization: Enter percentages to represent the proportions of surface water (4a.) and (4b.) groundwater (4b.) withdrawn for source water supply. Remember that the total of the two percentages must equal 100%.

  - Population Served: The retail population data is auto populated from the Water Use Survey.

  - Utility’s Length of Main Lines, miles: List the total length of pipeline in the water distribution system in miles.

  - Number of Retail Metered Connections Served: This number is auto populated from data entered in the Water Use Survey. Lists the number of active plus inactive retail customer connections served by the utility’s water distribution system. Connections as defined by Texas Administrative Code 290.38(16).

  - Service Connections: Number of customer service connections, extending from the water main to supply water to a customer. This includes the actual number of distinct piping connections, including fire connections, active and inactive. Do not include the total length of piping supplying fire hydrants - this should be included in the Length of Main Lines. Note: this may be different than the number of connections as defined by Texas Administrative Code 290.38(16).

  - Service Connection Density: Calculates the service connection density by dividing the number service connections by the length of miles of pipeline in the water distribution system.

  - Average Yearly System Operating Pressure: List the average pressure across the entire water distribution systems for the audit period. If a hydraulic model of the network exists, the average pressure can be calculated by the model; otherwise, an estimate can be used.

  - Volume Units of Measure: The volume unit of measure used throughout the Water Loss Audit form is gallons. Ensure that any values entered are in gallons.

- System Input Volume: The total water supplied to the distribution system. It is the total of all production meter readings for the entire year. List the volume or percentage requested in each item, along with the scores from Appendix 1.3 that in your judgment best represent the degree of validation of the data.

- Volume of Water Intake: Includes all water taken as source water from permitted sources, such as rivers, lakes, streams, and wells. This volume is obtained from the Water Use Survey and is for reference purpose only.

- Volume Treated VT: The volume of treated water input to distribution system from own production facilities.

13a. Volume Treated Meter Accuracy VTMA (enter a percentage): Achieved by calibrating or verifying the accuracy level (expressed as a percentage) of production meters. For example purposes, if the meter over-registered by 4 percent, enter 104; if it under-registered by 4 percent, enter 96.

13b. Corrected Volume Treated (calculated automatically online): The sum obtained when the production meter adjustment is either added to or subtracted from the system input volume. This value is auto-calculated.

Example: If “water volume from own sources” registered 1.8 MG/year through two production meters, which were found to be collectively under-registering flow by 4 percent, then the corrected input volume (CIV) is:

Corrected Input Volume = (1,800,000) ÷ (.96) = 1,875,000 – 1,800,000 = 75,000.

The additional 75,000 gallons was not registered by the meter.

- Treated Purchased TP: Amount of purchased wholesale water transferred into the utility’s water distribution system from other water suppliers. This is obtained from the Water Use Survey.

14a. Treated Purchased Meter Accuracy TPMA (enter a percentage): Achieved by calibrating or verifying the accuracy level (expressed as a percentage) of purchase meters. For example purposes, if the meter over-registered by 4 percent, enter 104; if it under-registered by 4 percent, enter 96.

14b. Corrected Treated Purchased (calculated automatically online): The sum obtained when the production meter adjustment is either added to or subtracted from the purchased water volume. This value is auto-calculated.

- Treated Sales (Wholesale) TS from Produced Water: This volume is auto populated from the Water Use Survey. Amount of wholesale water transferred out of the utility’s distribution system. It may be put into the system initially but is only in the system for a brief time for conveyance reasons.

15a. Treated Sales Meter Accuracy TSMA (enter a percentage): Achieved by calibrating or verifying the accuracy level (expressed as a percentage) of wholesale meters. For example purposes, if the meter over-registered by 4 percent, enter 104; if it under-registered by 4 percent, enter 96.

15b. Corrected Treated Sales (calculated automatically online): The sum obtained when the production meter adjustment is either added to or subtracted from the wholesale water volume. This value is auto-calculated.

15c. Percent of Treated Sales Transported Sales through the Treated Distribution System (enter a percentage): Total percentage of volume that is conveyed through the potable water distribution system and then metered to the wholesale customer. If you serve a wholesale customer with a direct line that is not conveyed through the distribution system, do not enter a percentage for that wholesale customer.

- Total System Input Volume: Calculated as the corrected input volume plus treated water purchased minus treated wholesale water sales. (Line 13b, plus Line 14b, minus Line 15b). The volume unit of measure should be gallons. This value is auto-calculated.

- Authorized Consumption: All water that has been authorized for use or consumption by the utility or its customers. Remember to enter these volumes in gallons.

- Billed Metered BMAC: All retail water sold and metered. This is obtained from the Water Use Survey.

- Billed Unmetered BUAC: All water sold but not metered.

- Unbilled Metered UMAC: All water metered but not billed, such as parks, golf courses, and municipal government offices.

- Unbilled Unmetered UUAC: All water not billed or metered, such as firefighting, flushing of water mains and sewers, street cleaning, fire flow tests, etc. Many activities may not be quantified therefore an industry standard default is recommended for temporary use. It is recommended to begin tracking and estimating these uses. The default is 0.25% of Billed Authorized Consumption (Billed Metered

+ Billed Unmetered). A value of zero is not permitted, since all water utilities likely have some volume of unbilled unmetered usage occurring.

- Total Authorized Consumption: The total of the above four components, automatically calculated in the online worksheet.

- Water Loss: Water delivered to the distribution system that does not appear as authorized consumption.

- Calculated as the difference of the system input volume and total authorized consumption (Line 16 minus Line 21).

- Apparent Loss: Water that has been consumed but not properly measured or billed. These losses represent under-registered or under-billed water that occurs via customer meter inaccuracy, systematic data handling error in the customer billing system, and unauthorized consumption:

- Customer Meter Accuracy CMA: List the composite accuracy percentage for your customer’s meters. This percentage is typically derived from meter testing results. A representative assessment of customer meter accuracy can be obtained by testing as few as 50 meters.

- Customer Meter Accuracy Loss: The percentage is multiplied by the sum of Billed Metered and Unbilled Metered to obtain the volume of loss due to customer meter inaccuracy.  (Line 17 + Line 18 ÷ Line 23). This is auto-calculated.

Example: If billed metered (line 17) consumption registered 1.5 MG/year and random meter testing found customer meters to be collectively under-registering flow by 8 percent, then the customer meter inaccuracy loss is:

Customer Meter Accuracy Loss = [(1,500,000) ÷ (.92) – 1,500,000] = 130,434.782 gallons. The 130,435 represents water that was not registered by the meter.

- Systematic Data Handling Errors SDHE: Apparent losses caused by accounting omissions, errant computer programming, gaps in policy, procedure, and permitting/activation of new accounts; and any data laps resulting in under-stated customer water use in summary billing reports. If the auditor does not have detailed data on these errors, it is recommended to use the industry standard default value. It is recommended to begin tracking and estimating these volumes. The default is 0.25% of Billed Authorized Consumption (Billed Metered + Billed Unmetered). A value of zero is not permitted, since all water utilities likely have some volume of data handling errors occurring.

- Unauthorized Consumption UC (theft): Includes an estimate of water taken illegally from fire hydrants, illegal connections, customer meter bypasses, meter/meter reading equipment tampering, or other unauthorized uses that prevent the utility from collecting revenue for the water. In most utilities it is a small portion. If the auditor has not gathered detailed data on these unauthorized uses, it is recommended to use the industry standard default value. The default is 0.25% of Billed Authorized Consumption (Billed Metered + Billed Unmetered). A value of zero is not permitted, since all water utilities likely have some volume of unauthorized consumption occurring.

- Total Apparent Losses: This value is calculated automatically online as the sum of customer meter accuracy loss, systematic data handling error, and unauthorized consumption.

- Real Loss: These are physical losses from the pressurized water distribution system, including water mains and all appurtenances (for example, valves and hydrants) and customer service connection piping. Real losses represent water that is lost from the distribution system prior to reaching the customer destination.

- Reported Breaks and Leaks: Reported breaks and leaks are brought to the attention of the water utility by customers, public safety officials, other utilities, or other members of the general public. Usually these visible water main breaks are very disruptive and water utilities respond quickly to these events, so the run duration of the break or leak is relatively short. Estimate the total volume of water loss during the water audit period from reported breaks and leaks that were repaired during the year. Leakage flow rates must be estimated for various types of breaks and leaks, as well as the approximate duration of the breaks or leaks prior to repair.

- Unreported Loss: This is a “catch-all” volume, meaning that this volume of real losses is the quantity that remains after authorized consumption, apparent losses, and reported leakage have been subtracted from the system input volume. In every water distribution system, even those employing effective active leakage control programs, experience some amount of undetected leakage. Some of this loss is comprised of unreported leakage that has not yet been detected in leak surveys. It also includes a subcomponent known as background leakage, which is the collective weeps and seeps at pipe joints and on customer service connections that cannot be detected with acoustic sounding devices. Any degree of error in quantifying metered and estimated volumes in the water audit results in error in this component. As the validation of the water audit improves over time, so will the level of validation of the unreported leaks volume.

- Total Real Loss: This value is calculated automatically online as the sum of reported breaks and leaks and unreported loss. Line 28 + Line 29

- Water Loss: Calculated as the sum of apparent losses and real losses. This value should equal the value of Line 22. This line is included as a balancing check. Line 27 + Line 30

- Non-revenue Water: Calculated as the sum of apparent losses, plus real losses, plus unbilled metered consumption and unbilled unmetered consumption. This is the water that does not contribute to water utility billing. Line 31 + Line 19 + Line 20

- Technical Performance Indicator for Apparent Loss: Performance indicators are quantitative measures of key aspects within the utility. Using these indicators, the utility will have a history to track its performance from year to year. One performance indicator exists for apparent loss.

- Apparent Loss per Connection per Day (Apparent Losses Normalized): Calculated as the volume of apparent loss (Line 27), divided by the number of service connections (Line 8), divided by 365 days. This performance indicator allows for reliable performance tracking in the water utility’s efforts to reduce apparent losses. Line 27 / Line 8 / 365

- Technical Performance Indicator for Real Loss: Several performance indicators exist for real loss.

- Real Loss Volume (Total Real Loss): This is the quantity from Line 30.

- Unavoidable Annual Real Losses (UARL): Calculated reference value using the equation shown in Table 3-2 of the Texas Water Loss Manual, which is found at the bottom of the page using the following link, www.twdb.texas.gov/conservation/Municipal/waterloss/index.asp. This is a theoretical value of the technical low level of leakage that might be attained in a water utility, based upon several specific parameters.

((Lm)(5.41)(365) + (Nc)(0.15)(365)) (P) = UARL

Lm = Length of main lines (Line 6)

Nc = Number of service connections (Line 7b) P = Average operating pressure (Line 11)

The UARL may not be effective for utilities having less than 3,000 service connections and is therefore not calculated.

- Infrastructure Leakage Index ILI: This performance indicator is calculated as the ratio of real losses over the unavoidable annual real losses. The index measures the water utility’s leakage management effectiveness and is an excellent performance indicator for comparing performance among water utilities. The lower the value of the infrastructure leakage index, the closer the utility is operating to the theoretical low level of the unavoidable annual real loss. Appendix 1.3 gives general guidance on setting preliminary leakage reduction targets using the infrastructure leakage index without changing water pressure. The ILI may not be effective for utilities having less than 3,000 service connections and is therefore not calculated. Line 34 / Line 35

ILI = Total Real Loss/UARL

- Real Loss per Connection per Day (Real Losses Normalized): Calculated as the real loss volume, divided by the number service connections, divided by 365. This indicator allows for reliable performance tracking in the water utility’s efforts to reduce real losses. Line 34 / Line 8 / 365

- Real Loss per Mile per Day (Real Losses Normalized): Calculated as the real loss volume, divided by the number of miles of pipeline, divided by 365. This calculation is used if the service connection density is less than 32 per mile. This indicator allows for reliable performance tracking in the water utility’s efforts to reduce real losses. Line 34 / Line 6/ 365

I. Technical Performance Indicator for Water Loss:

- Total Water Loss per Connection per Day: Calculated as the water loss volume (Line 22), divided by the number service connections (Line 8), divided by 365. This indicator allows for reliable performance tracking in the water utility’s efforts to reduce water losses. Line 22 / Line 8 / 365

J. Financial Performance Indicators:

- Total Apparent Loss: Lists the volume from line 27.

- Retail Price of Water: Water utility rate structures usually feature multiple tiers of pricing based upon volume consumed. For the water audit, it is best to use a single composite price rate to represent the retail cost of water, which is used to place a value on the apparent losses. Where appropriate, use the tier with the majority of the consumption. Enter the price as $/gallon.

- Cost of Apparent Loss: Calculated by multiplying the apparent loss volume by the retail price of water. This represents the potential amount of missed revenue due to apparent losses. Line 40 X Line 41

- Total Real Loss: Volume populated from line 30.

- Variable Production Cost of Water: Marginal production cost is defined by only costs that vary based on amount produced. Variable cost, typically include the cost of raw water, energy, and chemicals. If applicable, the cost of raw water should include the price of take or pay contracts. For example, if you have ground water then you most likely only have the cost of chemicals and to get the water into distribution. Add the chemicals and electricity for the year and divide by Line 16, the Total System Input Volume. The answer is your cost of water per gallon. These costs are applied to determine the cost impact of real losses. In cases of water shortage, real losses might be valued at the retail price of water instead of the variable production cost.

- Cost of Real Loss: Calculated by multiplying the real loss volume by the variable production cost of water. These costs represent the additional operating costs incurred by the water utility due to the real losses (in other words, leakage). Line 43 X Line 44

- Total Cost of Water Loss: Calculated by adding lines 42 and 45. This amount indicates the cost inefficiency encountered by the water utility for losses. This cost value can be objectively weighed against potential loss control programs to determine the cost effectiveness of such programs.

K. Gallons per Capita per Day (GPCD) for Water Conservation Planning:

- Total GPCD Input: This is the volume of water produced Per Capita Daily in gallons and is calculated as the Total System Input Volume (Line 16) divided by the Retail Population Served (line 5).

- GPCD Loss: This is the volume of water lost Per Capita Daily in gallons and is calculated as total water losses (Line 31), divided by the retail population served (Line 5), divided by 365.

Comments: Any information pertinent to the system and/or the data in the audit may be entered here.

If you or the utility need(s) water loss assistance, please call our Water Loss Group at 512-463-0987 or email: WLA-Group@twdb.texas.gov.